## Slide 1: Turtle Hub Electric Grid Training

## Slide 2: Intro
This is theory
Practical training on-playa (Thursday of build week)
Ask questions! No rush!
Still confused? Write down slide #

## Slide 3: Intro
Wide range of experience, from actual electricians to complete newbies
Mostly the goal is just to learn practical stuff
  How to connect, operate, and troubleshoot our grid
There is very little actual physics and math here:
  Volts, Watts, and Amps
  Watts = Volts x Amps

## Slide 4: What's This?

## Slide 5: GENERATOR
Closed frame
120V
2200 Watts
(Available up to about 5000 watts)

## Slide 6: What's This?

## Slide 7: GENERATOR
Open frame
120V
13,000 Watts

## Slide 8: FOOD FORT BACKUP

## Slide 9: What's This?

## Slide 10: GENERATOR
Three Phase (we’ll get back to that…)
120 - 240 - 480 Volt
56,000 Watts
  (available up to about 500,000)

## Slide 11
What’s all this about Volts and Watts?

## Slide 12: WATTS VS VOLTS
VOLTS is like water pressure.
Standardized household: 120V
All household devices in US use 120V
They just “sip” or “gulp” depending on how much power they need
Battery: 1.5V
USB: 5.1V
European house: 240V

## Slide 13: WATTS VS VOLTS
WATTS: measures power.
  “Gallons per minute”
  Single LED: 0.02 watts
  Household light: 2 - 10 watts
  Refrigerator: ~300 watts
  One horse: 746 watts
  Window AC: 1000-1500
  Our sound system: 1000
  Hair dryer: 1500
  RV: 4000

## Slide 14: How many watts?
Most things say on them!

## Slide 15
Add up all the watts that your things need to determine how big a generator you get!

## Slide 16: WHAT IS THE DIFFERENCE BETWEEN THESE?
2awg 200 amps $1500
6awg 50 amps $500
12awg 15 amps $50
16awg 10 amps $20

## Slide 17: Wire Gauge
The thicker the wire, the more current it can carry (measured in amps)
Thinness is measured in awg. The higher the thinner.

## Slide 18: So what ARE amps?
AMPs = WATTs ÷ VOLTs
WATTs = ?
WATTs = AMPs x VOLTs
Determines wire size. Thicker wire carries more amps.
Household wiring, outlets, and breakers can handle 15 or 20 AMPS

## Slide 19: WHAT IS THE DIFFERENCE BETWEEN THESE?
2awg 200 amps $1500
6awg 50 amps $500
12awg 15 amps $50
16awg 10 amps $20

## Slide 20
What does a BREAKER protect?

## Slide 21
A BREAKER protects WIRES

## Slide 22
A BREAKER protects downstream WIRES

## Slide 23
It keeps them from burning up from too many AMPS

## Slide 24
It does not care if someone is getting shocked.

## Slide 25
Unless that would draw too many amps.
More about safety coming up soon.

## Slide 26: WHY ARE THERE FIVE WIRES COMING OUT OF THIS?

## Slide 27: Household 120V AC
Copper = Ground
Black = Hot
White = Neutral
Hot is where the
electricity “comes from”. Neutral is where it “goes back”

## Slide 28: THREE PHASE POWER
Green = Ground
Black, Red, and Blue = Hot
White = Neutral

## Slide 29: THREE PHASE POWER
Black + white = 120V
Red + white = 120V
Blue + white = 120 V
Any two hots = 208 V

## Slide 30: THREE TIMES THE FUN!

## Slide 31: Distribution
SPIDER
BOX
GeneratOR
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
SPIDER
BOX
DIST
PANEL
DIST
PANEL
SPIDER
BOX
SPIDER
BOX

## Slide 32: Distribution

## Slide 33: Distribution
GeneratOR
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
SPIDER
BOX
DIST
PANEL
DIST
PANEL
SPIDER
BOX
SPIDER
BOX

## Slide 34: 5 WIRE BANDED CABLE
GeneratOR
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
SPIDER
BOX
DIST
PANEL
DIST
PANEL
SPIDER
BOX
SPIDER
BOX

## Slide 35: DISTRIBUTION PANEL
DIST
PANEL
GeneratOR
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
DIST
PANEL
SPIDER
BOX
SPIDER
BOX

## Slide 36: 50 AMP CABLES
DIST
PANEL
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
DIST
PANEL
SPIDER
BOX
SPIDER
BOX
GeneratOR
4 CONDUCTORs
ONLY CARRY 2 of 3 LEGS

## Slide 37: Spider Box
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
SPIDER
BOX
DIST
PANEL
DIST
PANEL
DIST
PANEL
GeneratOR

## Slide 38: Spider Box

## Slide 39: What keeps us safe?
Breakers
  Protects the wires downstream from heat/fire
    Short Protection
      What is a short? Why are shorts so bad?
    Overload Protection
GFCIs
  Measure return current. Not enough? Someone is being electrocuted
Keeping shit out of water

## Slide 40: Oh no! some breaker flipped!
Instantly re-flips?
  Short!
Reflips after a minute?
  Overload!
Main breaker at the generator?
  Turn off ALL distros, flip generator on, then bring up one distro at a time.
Breaker at a distro?
  Turn off all branches (power to spider boxes), flip distro on, then bring up one spider box at a time
Breaker at a spider box?
  Turn off all breakers on the spider box, turn on spider box, then turn on breakers one at a time

## Slide 41: Mystery!
Everything was running fine.
We turn off the generator to check the oil.
Ten minutes later, we turn it on again.
The main breaker on the generator flips right off

## Slide 42: Startup power can be MANY TIMES MORE than running power (AC, PUMP, MOTOR, FRIDGE)
Anything with a motor

## Slide 43: "It doesn't work" diagnoses
Is the generator on?
Work your way back from the load
Testing tools
Multimeter
Plug in diagnostic

## Slide 44: Common Playa Problems
Generator is not tuned to 120, or too much voltage drop at the ends of the network
GFCI itself is faulty
Overload because of heavy load (AC, heater, motor, stove, fridge)
  Sometimes this is a fan or motor clogged with playa dust

## Slide 45: Measurement and test tools
outlet tester
multimeter - for volts only

## Slide 46: Measurement and test tools
clamp meter
  works on banded cables
  doesn't work on 50A or extension cords (why not)?
  but there is a tool to make it work on a regular outlet
generator SOMETIMES has meters built in
distribution panels SOMETIMES have meters built-in

## Slide 47: SAFETY
Wear boots with rubber soles
You may think you know the path of least resistance, but electricity always knows!

## Slide 48: SAFETY
Don’t let your knees touch the ground

## Slide 49: SAFETY
Use sockitboxes for all outdoor connections (plug into extension cord, power outlet, etc)

## Slide 50: SAFETY
“Anti Murder Screwdriver”
When you’ve got the generator turned off for maintenance, put a screwdriver through the lock latch of the control panel.
If you see that screwdriver there, do not turn on the generator and murder your fellow electrician.

## Slide 51: ARCING
HIGH CURRENT -> ARC DANGER
Don’t plug and unplug anything that is powered on
ESPECIALLY banded cable or 50 amp cables! Jeez!

## Slide 52: SAFETY
Flip breakers off before plugging or unplugging anything more than household current
Low loads can be plugged and unplugged while hot
Motors, ACs, etc may spark
50 amp / 200 amp plugs are not designed to be safe to plug and unplug while hot

## Slide 53: SAFETY
Don’t be LoveBurn
Don’t use household extension cords - only outdoor rated, 12awg or lower
Don’t plug extension cords into extension cords (this is a camper problem usually)

## Slide 54: SAFETY
Assume the ground is wet. Look at everything you see with that in mind

## Slide 55: SAFETY
Don’t coil excess high amp cables
That will make a magnet
Make a figure 8 instead

## Slide 56: Three phase load balancing (1/2)
Each distribution box splits up 3 legs into 2 legs per 50A circuit
Each spider box takes splits up 2 legs among all outlets
Measure load on each phase (in amps)
  clamp meter
Log that in a book
Move load from highest leg to other legs until they are closer together
  usually by moving a spider box from one outlet on the distribution panel to another outlet

## Slide 57: Three phase load balancing (2/2)
For convenience outlets, color lights above them indicate phase.
For 50amp outlets, each consecutive outlet uses different phases:
A | B | C | A
B | C | A | B
C | A | B | C

## Slide 58: Daily generator maintenance
Morning and evening:
  Fuel level (turn off generator before running out of fuel!!!!)
  Load balancing
Morning only:
  with generator off:
    oil check
    Coolant overflow tank, add water as needed
    Remove air filter, bang out dust, replace if it has been a dusty day
  Turn generator back on (ideally one distro at a time)
  Blow radiator out with leaf blower or air compressor

## Slide 59: Where does diesel fuel come from
BRC Petrol and other backup plans

## Slide 60: Our RV as emergency backup
Mainly for health and safety. We can run lighting and maybe audio if we have a party, but no ACs
Might keep reefer running
Has a single 50 amp outlet in one of the bays
RV generator would have to be running

## Slide 61: Food Fort Generator backup
This is the big open-frame generator that we use to run the walk in fridge from Reno to playa
But we don’t have any way to add fuel

## Slide 62: On Playa
Build team
In-person training and certification
Guidelines to your campers about permitted / non-permitted use and what to expect from the power system